## Inquiry
1.I/O Signal Breakdown (TPV1)
You mentioned 300 I/O points for TPV1. Could you please provide the breakdown by signal type?
Digital Inputs (DI): | 130
Digital Outputs (DO): | 50
Analog Inputs (AI): | 100
Analog Outputs (AO): | 20
2. I/O Point Count (TPV3)
When do you expect to provide the TPV3 point count? We can issue a preliminary quotation for TPV1 now and update it once TPV3 data is available, if preferred.
REPLY:Within 3–5 days. Please provide a quotation only for TPV1 first and updated it once TPV3 is available. Approximately how much additional cost should we expect for TPV3 compatibility?
3. Number of Operator Workstations
From the network diagram, we see one AWS (laptop). Please confirm:
Is this the only operator workstation, or are additional workstations planned?
REPLY:Only operator workstation
Do you require remote/web-based access to the SCADA system (e.g. from an office or control room)?
REPLY:Not required
4. Communication Protocol
Based on the diagram, the AWS communicates with both S7-1200 PLCs via Ethernet (TCP/IP over fiber optic). Alpha SCADA supports Siemens S7 Communication protocol natively, which is the recommended option for S7-1200 CPUs. Please confirm this is acceptable.
REPLY:Acceptable
5. Server Redundancy
Do you require a redundant (backup) SCADA server for failover, or is a single-server configuration sufficient?
REPLY:a single-server configuration is sufficient
6. Data Logging (Historian)
You mentioned data logging as a requirement. Could you specify:
Approximate data retention period (e.g. 1 year, 5 years)
Logging frequency / scan rate (e.g. every 1 second, 5 seconds)?
REPLY:1 year; logging frequency/scan rate adjustable between 200ms and 500ms.
7. Reports
You mentioned data report export capability. Could you clarify:
What types of reports are needed (e.g. daily/monthly summaries, alarm reports, trend reports)?
Export format preference (PDF, Excel, CSV)?
REPLY: Daily summaries, alarm reports, trend reports; Export format preference Excel
8. Technical Support & Warranty
Regarding the 5-year warranty period — does this refer to:
Software license validity (perpetual license with 5 years of updates)?
Technical support contract (SLA) for 5 years?
Or both?
REPLY:Perpetual license, no need for 5 years of updates. Technical support is required. How many years is the default technical support period? Please provide a quotation based on the default technical support period, and also give a quotation for 5 years of technical support.
Please let us know your preferred support level:
Basic — software updates only
Standard — updates + remote technical support during business hours
Extended — updates + priority support with guaranteed response time
REPLY:Please provide us with quotations for these three,a comprehensive consideration is needed.
9. Timeline
What is your expected project timeline / desired delivery date for the software?
REPLY:within 1 month